## Sheet1
Site | Category | Observation | Location
95 | 2 | Acoustic enclosure is required for the Air blowers. | STP Pump room
95 | 2 | FRP make drain cover is suggested instead of MS gratings to avoid corrosion and increase the life span of the cover. Pit to be provided with tile cladding. | STP Drain pit chamber
95 | 2 | STP Final tank overflow pipe line is connected to the STP drain pit. This has to be connected to basement drain to avoid water ingression to the pump room. | STP Pump room
95 | 3 | FRP grills are required for the WSP drain pit, instead of the present installed MS grills to avoid corrosion and ensure long life of the grills | WSP - Drain Pit
95 | 3 | Online pressure pump is required to pump the brine solution to the softener during the regeneration process as the present ejector system is not effective. Eg. Cyber Life WSP. | WSP - Softener
95 | 3 | Cob webs on Softener to be cleared and the external surface of the vessel to be cleaned. Seepage to be arrested. | WSP - Softener
95 | 9 | Bore well details, Pump capacity, depth, casing depth, Pipe Size, water yield and the recent ground water depth etc… displayed at the respective bore well. | Bore wells
95 | 5 | No marking on 'Diesel level gauge' | Fire Pump Room
95 | 5 | DG Exhaust to be extended to podium level. Right now it was extended just outside the pump house | Fire Pump Room
95 | 5 | Sequence of pump operation, pump capacities and connected tank capacities to be provided in Fire pump room | Fire Pump room
95 | 5 | De-watering pump to be provided in fire pump | Fire Pump room
95 | 5 | Pump room electrical panel SLD to be provided | General
95 | 5 | Fire Alarm, group indication panel routing and SLD to be provided | General
95 | 5 | Emergency Escape Route Plan to be displayed at Designated locations. | Fire Safety
95 | 11 | Metro water supply connection to be given
95 | 11 | Swimming pool to be commisioned and handed over
95 | 11 | Water bodies to be commisioned and handed over.
95 | 11 | Pre-paid Energy Meter system to be commisioned and handed over
95 | 11 | CCTV System to be commisioned and handed over
95 | 11 | Boom Barrier System with RFID system to be commisioned and handed over
95 | 11 | Water meters and Billing system to be commisioned and handed over. Consumption and billing to be done for existing occupants for atleast two months
95 | 11 | Speed breakers & traffic signage to be placed
95 | 11 | Garbage dumping location to be provided on podium with fresh water and drainage.
95 | 11 | MS type openable cover to be provided for Metro water meter chamber pit.
95 | 11 | All the statutory certificates from government and as-built drawings of project to be handed over.
95 | 10 | Railing with entry gate to be provided around the swimming pool for safety of children not to enter the pool.
95 | 10 | Life -buoy rings to be provided near swimming pool.
95 | 10 | Fresh water & Drain to be provided for pedicure in Saloon
95 | 10 | Notice board to be provided in Club house reception.