## Sheet1
Submersible Bore well pumps/motors 09.02.2019
S.No | Bore well Number | Depth | YIELD (at the time of installation) | Date Drilled | HP | KW | Borewell status | Location | Motor | HTP PIPE | Cable | Ring Line Connectivity | Pipe type | Flowmeter installed | Recent Update | Past History | Motor status | Issue | Resolution | Update on 09.02.2019
1 | 2 | 710 ft | 3" | 2007-09-05 | 10 | 7.5 | Not working | Sub-cellar in front of STP pump room | Removed | Damaged | Damaged | OK | HDPE 2" | Yes | 1. New motor - Falcon make - 10HP installed in ____. 2. Electronic starter fixed in Nov 2018 by Mr.KP Reddy for voltage improvement. Old borewell flat cable 2 runs laid from ventilation system to borewell point by Mr.KP Reddy. | 1. New cable of 4 sq.mm, 3 core flat cable laid in March 2016 from submersible pump to surface area. 2. Motor was repaired in 2016. Not working even after repair. | Not working | 1. Consuming High current since 10th Dec 2018. Drawing 26.99 Amps. Relay setting is 25 Amps. 2. Keeps tripping. | Called vendor as it is still under warranty | Resistance RY 43 YB 48 BR 51 Phase volt Line Volt RY 43 RN 234.7 YB 48 YN 237.1 BR 51 BN 235.8 Star currents Delta currents R 23.0 R 30.35 Y 21.64 Y 29.25 B 22.61 B 31.05 Borewell no 2 taking high currents
2 | 3 | 605 ft | 4" | 2007-10-05 | 10 | 7.5 | Not working | At cellar Near STP entrance |  |  |  | OK | GI 2" | Yes |  | 1. New cable of 4 sq.mm, 3 core flat cable laid in 2016 from submersible pump to surface area. 2. Motor was repaired in 2016. Motor worked for only 1 year. | Not working | Winding burnt. Due to that starter also got burnt | 1. Motor to be extracted for repairing. 2. New starter to be purchased. | Starter got internally flash over now starter not working Resistance RR 120.6 YY 85.7 BB 63.0
3 | 4 | 560 ft | 4" | 2007-12-05 | 10 | 7.5 | Not working | At cellar Beside Mist fountain pump room |  |  |  | OK | HDPE 2" | Yes |  | 1. New cable of 4 sq.mm, 3 core flat cable laid in March 2016 from submersible pump to surface area. 2. Motor was repaired in 2016. Not working even after repair. | Not working | 1. Consuming High current . Drawing 66 Amps. Relay setting is 20 Amps. 2. Keeps tripping. | 1. Motor to be extracted for repairing. 2. New starter to be purchased. | Motor winding Burnt Starter working good.
4 | 5 | 410 ft | 2.5" | 2007-12-05 | 10 | 7.5 | Not working | At cellar near H block car wash area |  |  |  | OK | HDPE 2" | Yes |  | 1. New cable of 4 sq.mm, 3 core flat cable laid in March 2016 from submersible pump to surface area. 2. Motor was repaired in 2016. Not working even after repair. | Not working | 1. Consuming High current . Drawing 70-80 Amps. Relay setting is 20 Amps. 2. Keeps tripping. | 1. Motor to be extracted for repairing. | Motor winding Burnt Starter working good.
5 | 6 | 600 ft | 2" | 2007-08-20 | 10 | 7.5 | Not working | Center podium-cellar near U/G sump |  |  |  | OK | HDPE 2" | Yes |  |  | Not working | 1. Showing single phase indication (i.e. other phase failed). 2. Over current is also indication but the currents (13.8 A) are normal | To be checked by vendor | Voltage RY 409 YB 410 BR 415 Resistance Currents RY 3.9 R 16.8 YB 3.7 Y 16.8 BR 3.6 B 17.1 Starter was tripping after 30 minutes due to over load and single phase
6 | 7 | 600 ft | 2" | 2007-08-18 | 7.5 | 5 | Not working | Center podium-cellar beside U/G sump | strucked | OK ( 480 ft ) | OK | OK | HDPE 2" | Yes |  | 1. Pipe was cut while extracting at 480 mts. Motor was stuck on 29.02.2016. 2. New motor installed 3. New cable of 4 sq.mm, 3 core flat cable laid in March 2016 from submersible pump to surface area | Working | 1. Tripping due to dry run (probably low yield) | To be checked in monsoon (July 2019) | Resistance RY 5.1 YB 6.4 BR 6.0 Voltage Currents RY 409 R 13.1 YB 410 Y 13.2 BR 415 B 12.8 Starter tripping after 45 minutes due to dry run Voltage Currents RY 408 R 13.2 YB 410 Y 14.1 BR 412 B 13.7
7 | 8 | 600 ft | 4" | 2007-08-18 | 10 | 7.5 | Not working | At sub cellar opp WTP |  |  |  | OK | HDPE 2" | Yes |  |  | Working | 1. Tripping due to dry run (probably low yield) | To be checked in monsoon (July 2019) | Voltage Currents RY 408 R 13.2 YB 410 Y 14.1 BR 412 B 13.7 Resistence RY 10.7 YB 10.5 BR 10.3 Starter tripping due to dry run
8 | 10 | 450 ft |  | 2007-08-17 | 10 | 7.5 | Running | At cellar near L block ramp |  |  |  |  | HDPE 2" | Yes |  |  | Not working | 1. MPCB getting tripping due to motor winding or cable short circuit | Motor to be extracted to find the fault. | Voltage Currents RY 408 R 11.3 YB 410 Y 11.8 BR 412 B 11.1 MPCB tripped due to motor internal problem
9 | 10A | 450 ft | 2" | 2007-08-19 | 10 | 7.5 | Running | M block Cellar near storm water sump |  |  |  |  | HDPE 2" | Yes |  |  | Not working | 1. Winding got burnt | Motor to be extracted and re-winding to be done. | Motor winding got burnt
10 | 11 | 600 ft | 4" |  | 10 | 7.5 | Not working | North East corner on ground floor ( L lock water court ) | Removed | OK | Damaged | NA | HDPE 2" | Yes | New motor installed in July 2018 | Motor was extracted on 29.02.2016, but not installed back. | Working |  |  | Currents R 19.9 Y 18.0 B 19.3 Motor taking normal current
11 | 12 | 130 ft |  |  | 5 | 4 | Running | Beside F block Exit ramp |  |  |  | OK | HDPE 2" | Yes |  | 1. New motor installed in March 2016. 2. New cable of 4 sq.mm, 3 core flat cable laid in March 2016 from submersible pump to surface area. 3. HDPE pipe 400 feet procured. But only 130 feet went inside. Remaining cut and handed over to ASOWS. | Working |  |  | GOOD
12 | 14 | 600 ft | 4" | 2007-08-16 | 10 | 7.5 | Running | At cellar Center podium-cellar ,near STP |  |  |  |  | HDPE 2" | Yes |  |  | Working |  |  | GOOD
13 | 16 | 450 | 2" | 2009-08-24 | 10 | 7.5 | Not working | Beside D block Gas Bank | Removed | OK | Damaged | NA | HDPE 2" | Yes |  | 1. New cable of 4 sq.mm, 3 core flat cable laid in March 2016 from submersible pump to surface area. 2. Motor was repaired in 2016. Not working since Oct 2018 3. There is hole in GI pipeline. Repaired in 2017 | Not working | 1.The motor tripping due to high currents (53 A) | Motor to be extracted to find the fault. | Starter tripped due to single phase and over load
S.No | Bore well Number | Depth | YIELD (at the time of installation) | Date Drilled | HP | KW | Status | Location | Motor | HTP PIPE | Cable | Ring Line Connectivity |  |  |  | Remarks
1 | 1 |  |  | 2007-09-05 |  |  | Closed | A block sub cellar
2 | 9 | [5 empty] | Closed | club house inside Squash court
3 | 13 | [5 empty] | Closed | Near 5 panel
4 | 15 | [5 empty] | Closed | At Ground floor Near E block

## Sheet2
Bore well 09.02.2019
S.No | Bore well Number | Depth | HP | KW | Borewell status | Location
1 | 2 | 710 ft | 10 | 7.5 |  | Sub-cellar in front of STP pump room
2 | 3 | 605 ft | 10 | 7.5 |  | At cellar Near STP entrance
3 | 4 | 560 ft | 10 | 7.5 |  | At cellar Beside Mist fountain pump room
4 | 5 | 410 ft | 10 | 7.5 |  | At cellar near H block car wash area
5 | 6 | 600 ft | 10 | 7.5 |  | Center podium-cellar near U/G sump
6 | 7 | 600 ft | 7.5 | 5 |  | Center podium-cellar beside U/G sump
7 | 8 | 600 ft | 10 | 7.5 |  | At sub cellar opp WTP
8 | 10 | 450 ft | 10 | 7.5 |  | At cellar near L block ramp
9 | 10A | 450 ft | 10 | 7.5 |  | M block Cellar near storm water sump
10 | 11 | 600 ft | 10 | 7.5 |  | North East corner on ground floor ( L lock water court )
11 | 12 | 130 ft | 5 | 4 |  | Beside F block Exit ramp
12 | 14 | 600 ft | 10 | 7.5 |  | At cellar Center podium-cellar ,near STP
13 | 16 | 450 | 10 | 7.5 |  | Beside D block Gas Bank
S.No | Bore well Number | Depth | HP | KW | Status | Location
1 | 1 |  |  |  | Closed | A block sub cellar
2 | 9 |  |  |  | Closed | club house inside Squash court
3 | 13 |  |  |  | Closed | Near 5 panel
4 | 15 |  |  |  | Closed | At Ground floor Near E block

## Sheet3
Bore well Number | 2
Depth
YIELD (at the time of installation)
Date Drilled
HP
KW
Borewell status
Location
Motor
HDPE PIPE
Cable
Ring Line Connectivity
Pipe type
Flowmeter Status
Recent Update
Motor status

## Sheet4
S.No
Bore well Number
Depth
YIELD (at the time of installation)
Date Drilled
HP
KW
Borewell status
Location
Motor
HTP PIPE
Cable
Ring Line Connectivity
Pipe type
Flowmeter installed
Recent Update
Past History
Motor status
Issue
Resolution
Update on 09.02.2019