## Instructions
Incident Timeline, Contacts & Root Cause Analysis
INSTRUCTIONS Go to the next worksheet page for the Template
WARNING - IN DESCRIBING AN INCIDENT BE SURE TO ONLY REPORT FACTS, NOT YOUR OPINIONS. AN INCIDENT REPORT AND ALL DOCUMENTS ASSOCIATED WITH AN INCIDENT CAN BE CALLED FOR BY LAW COURTS AND CAN BE USED AS EVIDENCE AGAINST OUR FIRM. YOUR OPINIONS MAY ADVERSELY IMPACT OUR FAIR DEFENCE. IF IN DOUBT CONTACT JLL LEGAL.
Root Cause Analysis (RCA) is a structured, step-by-step technique that focuses on finding the real cause of a problem and dealing with that, rather than continuing to deal with it's symptoms. It is an obligation of property/facility teams to conduct a RCA analysis each time any incident with a severity level (ISL) of Level 2 or 3 occurs, though it may be used at any time as a technique for analysis of any performance or system failure.
A RCA investigation must be completed using this template and be attached to the OneViewRiskManagement report. The report uses the "5 Whys?" technique of RCA to find the "root" cause of a failure, not just what may appear to be the immediate cause.
More than one report may be lodged for an incident depending on the complexity of the failure chain being reported.
Investigation into all background information is required for the RCA, or for use by a specialised team possibly including consultants and/or manufacturers representatives. Preparation of background material may include log data, photographs, drawings and diagrams, as required.
Under the "Timeline of Events" section, the situation in which the failure occurred must be reported. This includes details of operating conditions, the configuration or layout of equipment, environmental conditions and advice on whether these circumstances were normal or abnormal.
How the failure/incident was discovered must be reported in the "Timeline of Events."
The effect on safety, Business Unit operations or reliability needs to be reported. This indicates the importance of the failure and the urgency for recovery action. How the failure occurred will sometimes be easily identified and reported on early during the incident reporting process, if sufficient evidence and knowledge is available. However, the logical steps leading to the failure/incident and identification of the root cause will often require more detailed investigation.
The root cause findings and recommendations must be clearly stated to permit the RCA to be a 'stand alone' document. This part may include recommendations for further technical assessment to be used to initiate a repair, modification or rework project. The findings must not include anything that is not reported or discussed in earlier sections of the report.
When completing the RCA report:
* Start at the top of the report and work your way down through the form.
* Make use of the hints given in the comments for many cells.
* Use the drop-down responses if they provide acceptable answers. If the selection options aren't suitable then select "Other" and submit your own response.
* Select one of the six failure classes that best describes the root cause of the failure. This may be identified only after the RCA analysis has been completed.
* For the Timeline of Events give a brief description of the events that happened, not an analysis of why the event happened. This area is meant to describe the facts of the events, not your reasoning of why.
In the first Root Cause Analysis (5 Whys) area use the first column field to generally describe what happened and use the second column field to describe what was the cause of it happening (Why 1).
In the second Root Cause Analysis (5 Whys) row use the first column field to describe what happened to cause the Why 1 event and use the second column field to describe what was the cause of it happening (Why 2).
In the third Root Cause Analysis (5 Whys) row use the first column field to describe what happened to cause the Why 2 event and use the second column field to describe what was the cause of it happening (Why 3).
In the fourth Root Cause Analysis (5 Whys) row use the first column field to describe what happened to cause the Why 3 event and use the second column field to describe what was the cause of it happening (Why 4).
In the fifth Root Cause Analysis (5 Whys) row use the first column field to describe what happened to cause the Why 4 event and use the second column field to describe what was the cause of it happening (Why 5) .
After completing the RCA delete the Instruction and Sample worksheets and submit the report to OneViewRiskManagement

## RCA Template
Timeline, Contacts & Root Cause Analysis
Incident Identification
Country | City | Location/Facility/Property
OneViewRiskManagement incident number
Incident Start Date
Timeline of Events (add additional rows if required)
Local date | Local time | Response
| (24hr format - HH:MM) | (Describe the events that led up to the incident and the steps taken to control/restore the systems to normal)
Persons Involved in generating report & Contact Information (add additional rows if required)
Family Name | First Name | Description/Title | Home phone | Mobile Phone | eMail address
Root Cause Analysis - (5 'Whys' analysis)
Immediate phenomenon description | Why? 1 |  | Cause Category | Cause Detail | Standards exist | Applied
[5 empty] | No | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 2
[5 empty] | Yes | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 3
[5 empty] | Yes | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 4
[5 empty] | No | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 5
[5 empty] | No | No
Describe here if Cause Detail above is "Other"
Analysis Summary and Corrective Action
If the event was the result of equipment failure, indicate the following:
Equipment Description | Manufacturer |  | Model | Serial Number
Root Cause Description resulting from the "5 Whys" analysis:
Is there a workaround or temporary fix currently in place?
Describe the workaround (if a permanent solution is not immediately available).
Describe the permanent corrective action (What? Who? When?)
Post Problem Review (PPR)
Is a PPR or Forensic Investigation needed to determine the Root Cause or a Permanent Solution?
Meeting Information:
| PPR Leader: |  | Date: |  | Time:
[7 empty] | Yes | All | CPI FAILURES | Yes | Whole building evacuation | MACHINES | Machines
[7 empty] | No | Part | Interrupted Operations | No | Business Unit Evacuation | Lubrication failure | Methods
[9 empty] | Legal Notices | Unknown | Loss of data communications | Setting failure | Materials
[9 empty] | Fines |  | Loss of tele-communications | Parts/Ass'y failure | Manpower
[9 empty] | Death / Injury |  | Loss of Normal Power Supply | Insufficient capacity | Measurements
[9 empty] | Customs Violations |  | Loss of Conditioned Power Supply | Power failure | Environment
[7 empty] | Yes |  | Local Public Incidents |  | Loss of Emergency Power Supply | Fuses blown
[7 empty] | No |  | Negative Local Community Incidents |  | Loss of drinking water | Control malfunction
[7 empty] | Not applicable |  | Notice of Violations |  | Loss of sanitation/toilets | Design/commissioning problem
[9 empty] | Regulatory non-compliance |  | Loss of fire detection system/s | Other
[9 empty] | Negative community relations |  | Loss of fire suppression system/s | METHODS
[9 empty] | Move process ineffectiveness |  | Loss of lighting | Lack of policies and procedures
[9 empty] | Cleaning ineffectiveness |  | Loss of acceptable air quality | Lack of work instructions
[9 empty] | Event Management ineffectiveness |  | Loss of weather protection/enclosure | Lack of technical training
[9 empty] | Budget non-compliance |  | Flooding from water pipe/storage | Lack of soft skills training
[9 empty] | Other |  | Loss of treated water system | Improper equipment layouts
[11 empty] | Loss of waste water treatment | Parts premature failure
[9 empty] | KPI FAILURES |  | Loss of building fabric/structure | Insufficient stock levels
[9 empty] | SERVICE RELIABILITY |  | Loss of access/security system | Poor quality materials
[9 empty] | System Reliability |  | Loss of Comfort Cooling | Over aged materials
[9 empty] | Climate Control |  | Other | Structural defects
[9 empty] | Uninterrupted Operations |  |  | Other
[9 empty] | AUDIT SCORES |  |  | MANPOWER
[9 empty] | CFAM Audit (%) |  |  | Lack of technical skills
[9 empty] | Risk Key Element (%) Sites over 8.0 |  |  | Attitude problems
[9 empty] | Archibus Data Integrity (%) |  |  | Lack of team spirit/ownership
[9 empty] | Cleaning Effectiveness Audit (%) |  |  | Lack of equipment knowledge
[9 empty] | Energy Audit Score |  |  | Fatigue, stress, sickness
[9 empty] | FINANCIAL |  |  | Lack of communication/awareness
[9 empty] | Forecast v. Budget |  |  | Lack of relationship building
[9 empty] | Total HUB Spend (%) |  |  | Lack of org. objectives/goals
[9 empty] | MOVES & OCCUPANCY PLANNING |  |  | Other
[9 empty] | Occupancy Rate (%) |  |  | MEASUREMENTS
[9 empty] | Moves Effectiveness (%) Moves on Time |  |  | Gauges/meter malfunction
[9 empty] | Daily Moves Surveys (Max 5.0) Score |  |  | Calibration errors
[9 empty] | CUSTOMER AND CONSUMER SATISFACTION |  |  | Lack of history analysis tools
[9 empty] | Event Management |  |  | Measurement systems not in place
[9 empty] | Cafeteria & Vending |  |  | Lack of predictive knowledge
[9 empty] | Mail & Shipping |  |  | Insufficient measuring systems
[9 empty] | Workplace Satisfaction |  |  | Lack of policies and procedures
[9 empty] | Laboratory Satisfaction |  |  | Other
[9 empty] | Overall Satisfaction |  |  | ENVIRONMENT
[9 empty] | Other |  |  | Room facility temps. high/low
High humidity conditions
High dust conditions
Noise pollution
Smoke or haze pollution
Heavy rains/ typhoons/hurricanes
Fire/earthquake
Other

## RCA Sample
Timeline, Contacts & Root Cause Analysis (sample)
Incident Identification
Country | City | Location/Facility/Property
OneViewRiskManagement incident number
Australia | Sydney | MegaBank Building, 22 George Street |  |  | 24
Incident Start Date | 30 May 2007
Timeline of Events (add additional rows if required)
Local date | Local time | Response
| (24hr format - HH:MM) | (Describe the events that led up to the incident and the steps taken to control/restore the systems to normal)
30 May 2007 | 13:30 | The building evacuation siren sounded in the facility offices. Building occupants were required to immediately evacuate in accordance with the site's procedures.
30 May 2007 | 13:40 | The building evacuation was completed and all staff had moved 100 metres away to the adjacent emergency assembly area under the coordination of floor wardens and the site fire warden.
30 May 2007 | 13:42 | The local fire brigade truck arrived in response to the fire alarm.
30 May 2007 | 13:45 | Firefighers, the fire warden and the facility site leader investigated the source of the alarm and identified the activation of a smoke detector in Zone 4 (office toilet area).
30 May 2007 | 13:48 | Site FM leader confirmed that a plumber was working on-site repairing toilet pipework. There was evidence of unauthorized hot work activity (smoke and welding equipment). A smoke detector above the work area is showing an active pilot neon.
30 May 2007 | 13:55 | Fire alarm system is reset and site is declared safe by fire service. All tenants are advise that they can return to their normal activities.
Persons Involved & Contact Information (add additional rows if required)
Family Name | First name | Description/Title | Home phone | Mobile Phone | eMail address
Smith | Joe | Facility Manager | 02 12345678 | 14141414141 | joe.smith@ap.jll.com
Brown | John | Security guard | 020202020 | 1515151515 | john.brown@securityl.com
Root Cause Analysis - ("5 Whys" analysis)
Immediate phenomenon description | Why? 1 |  | Cause Category | Cause Detail | Standards exist | Applied
Whole of building evacuation resulted from actuation of the building's smoke detection system. | Plumber was welding in men's toilet repairing/modifying pipework and didn't isolate the smoke detector. |  | Methods | Lack of work instructions | Yes | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 2
Plumber was a substitute tradesman provided instead of our regular contractor. He knew of the need to isolate the smoke detection system but thought it was too much effort and that it would not be activated by his small amount of work. | He had not been inducted to the site to raise his awareness of the importance of his actions. |  | Manpower | Lack of communication/awareness | Yes | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 3
The staff member responsible for induction of the vendors didn't set it as a high priority because he didn't realize the potential consequences of any failure. | Staff had not been trained in house rules policy and had not been given a deadline for application of house rules policy. |  | Manpower | Lack of communication/awareness | No | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 4
A training timetable had been set up by the local site leader but had not been adhered to due to other projects taking a higher priority. | Unexpected project work and FM team staff absence had left the site team without time to allocate to training. |  | Manpower | Fatigue, stress, sickness | No | No
Describe here if Cause Detail above is "Other"
Phenomenon description | Why? 5
Site leader had not communicated to his manager of critical absence of staff to deal with unexpected project work. | Site leader was not sufficiently proactive in dealing with the staffing shortage and had withheld communication to his senior manager. |  | Manpower | Lack of communication/awareness | No | No
Describe here if Cause Detail above is "Other"
Analysis Summary and Corrective Action
If the event was the result of equipment failure, indicate the following:
Equipment Description | Manufacturer |  | Model | Serial Number
Root Cause Description resulting from the "5 Whys" analysis:
The Site FM Leader had not taken steps to permit time for house rules training of site staff. Consequently, as a result of inadequate contractor induction, a plumber had not applied suitable procedures to permit isolation of the smoke detection system while performing hot work.
Is there a workaround or temporary fix currently in place? |  |  | Yes
Describe the workaround (if a permanent solution is not immediately available).
Additional casual staff resources have been engaged to permit the local facility team to become fully trained in "house rules" , health & safety and vendor management procedures.
Describe the permanent corrective action (What? Who? When?)
Site leader to reassess time allocated to regular staff training by 30 June 2007. A staff training calendar to be in place by 1 July and Regional Technical Manager to facilitate training on Contractor Management during July 2007.
Post Problem Review (PPR)
Is a PPR or Forensic Investigation needed to determine the Root Cause or a Permanent Solution? |  |  |  |  | No
Meeting Information:
| PPR Leader: |  | Date: |  | Time:
[7 empty] | Yes | All | CPI FAILURES | Yes | Whole building evacuation | MACHINES | Machines
[7 empty] | No | Part | Interrupted Operations | No | Business Unit Evacuation | Lubrication failure | Methods
[9 empty] | Legal Notices | Unknown | Loss of data communications | Setting failure | Materials
[9 empty] | Fines |  | Loss of tele-communications | Parts/Ass'y failure | Manpower
[9 empty] | Death / Injury |  | Loss of Normal Power Supply | Insufficient capacity | Measurements
[9 empty] | Customs Violations |  | Loss of Conditioned Power Supply | Power failure | Environment
[7 empty] | Yes |  | Local Public Incidents |  | Loss of Emergency Power Supply | Fuses blown
[7 empty] | No |  | Negative Local Community Incidents |  | Loss of drinking water | Control malfunction
[7 empty] | Not applicable |  | Notice of Violations |  | Loss of sanitation/toilets | Design/commissioning problem
[9 empty] | Regulatory non-compliance |  | Loss of fire detection system/s | Other
[9 empty] | Negative community relations |  | Loss of fire suppression system/s | METHODS
[9 empty] | Move process ineffectiveness |  | Loss of lighting | Lack of policies and procedures
[9 empty] | Cleaning ineffectiveness |  | Loss of acceptable air quality | Lack of work instructions
[9 empty] | Event Management ineffectiveness |  | Loss of weather protection/enclosure | Lack of technical training
[9 empty] | Budget non-compliance |  | Flooding from water pipe/storage | Lack of soft skills training
[9 empty] | Other |  | Loss of treated water system | Improper equipment layouts
[11 empty] | Loss of waste water treatment | Parts premature failure
[9 empty] | KPI FAILURES |  | Loss of building fabric/structure | Insufficient stock levels
[9 empty] | SERVICE RELIABILITY |  | Loss of access/security system | Poor quality materials
[9 empty] | System Reliability |  | Loss of Comfort Cooling | Over aged materials
[9 empty] | Climate Control |  | Other | Structural defects
[9 empty] | Uninterrupted Operations |  |  | Other
[9 empty] | AUDIT SCORES |  |  | MANPOWER
[9 empty] | CFAM Audit (%) |  |  | Lack of technical skills
[9 empty] | Risk Key Element (%) Sites over 8.0 |  |  | Attitude problems
[9 empty] | Archibus Data Integrity (%) |  |  | Lack of team spirit/ownership
[9 empty] | Cleaning Effectiveness Audit (%) |  |  | Lack of equipment knowledge
[9 empty] | Energy Audit Score |  |  | Fatigue, stress, sickness
[9 empty] | FINANCIAL |  |  | Lack of communication/awareness
[9 empty] | Forecast v. Budget |  |  | Lack of relationship building
[9 empty] | Total HUB Spend (%) |  |  | Lack of org. objectives/goals
[9 empty] | MOVES & OCCUPANCY PLANNING |  |  | Other
[9 empty] | Occupancy Rate (%) |  |  | MEASUREMENTS
[9 empty] | Moves Effectiveness (%) Moves on Time |  |  | Gauges/meter malfunction
[9 empty] | Daily Moves Surveys (Max 5.0) Score |  |  | Calibration errors
[9 empty] | CUSTOMER AND CONSUMER SATISFACTION |  |  | Lack of history analysis tools
[9 empty] | Event Management |  |  | Measurement systems not in place
[9 empty] | Cafeteria & Vending |  |  | Lack of predictive knowledge
[9 empty] | Mail & Shipping |  |  | Insufficient measuring systems
[9 empty] | Workplace Satisfaction |  |  | Lack of policies and procedures
[9 empty] | Laboratory Satisfaction |  |  | Other
[9 empty] | Overall Satisfaction |  |  | ENVIRONMENT
[9 empty] | Other |  |  | Room facility temps. high/low
High humidity conditions
High dust conditions
Noise pollution
Smoke or haze pollution
Heavy rains/ typhoons/hurricanes
Fire/earthquake
Other